## RealEstate
id | class | locatedAt | popularName | littera | aliasId
a60c8db5-ac33-4a04-9564-1694a08567de | RealEstate | 59.333239;18.061099;10 | Great view estate | 123 Great view estate | 123
…
UUID that identifies the ral estate | Type | Where he real estate is located (in WGS84) | Popular name for the real estate | Littra on blueprint | Id in e.g. building automation system

## BuildingStructure
id | class | belongsTo | locatedAt | popularName | littera | aliasId
3b6fec14-043b-4ecc-b6aa-b1255039388a | BuildingStructure | a60c8db5-ac33-4a04-9564-1694a08567de | 59.333539;18.061699;10 | Main Building | 123-001 Main Building | 123-001
…
UUID that identifies the building structure | Type | What RealEstate the BuildingStructure belongs to | Where he real estate is located (in WGS84) | Popular name for the BuildingStructure | Littra on blueprint | Id in e.g. building automation system

## BuildingStructureComponent
id | class | locatedIn | littera | storeyLevel | locatedAtLocalCoordinates | aliasId | comment:tagList
63e58b79-eeb2-4717-a66d-2b615e2dea4e | MainEntrance | 3b6fec14-043b-4ecc-b6aa-b1255039388a | 123-001-002 | 1 | 0;5;0,5 | 123-001-002
1bb52784-c9ed-4d16-b678-63127a02060d | ClimateControlRoom | 3b6fec14-043b-4ecc-b6aa-b1255039388a | 123-001-001 | 2 | 5,3;32,4;4,5 | 123-001-001
…
UUID that identifies the room | Type of room | What BuildingStructure the room (BuildingStructureComponent) is located in | Littra on blueprint | Storey level | The internal coordinates for the (center of the) room | Id in e.g. building automation system | Some comments from the blueprint or building automation sytem

## Device
General | [10 empty] | System specific
id | class | isPartOfDevice | locatedIn | servedBy | placementContext | deviceFunction | powerSource | quantityKind | auctionInterface | littera | source:localEndpointID | deviceCommunication | source:iPAddress | source:iPAddressPort | source:modbusNodeID | source:modbusRegister | source:modbusRegisterLength | source:scaleFactor | source:offset | source:product | source:modbusFunctionCode | source:comment
f660f703-6bf4-452f-8b4c-93e71f6ad82a | Device |  |  | 8f74f492-c82a-4c22-9c4e-9bd8360b544f |  | AirDiffuser | CommunicationBus |  |  | LB01-01-123-001-002 | 11002 | ModbusTCP | 10.32.6.220 | 502 | 1 |  |  |  |  | LindInvent TTC
1a2d076a-ab61-44b0-9285-a6b96a45a37e | Actuator | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | Indoor |  | CommunicationBus | Temperature | Number |  | 11002 |  |  |  |  | 21 | 1 | 10 | 30000 |  | 3.6 | Setpoint for room ttemperature
db7fa80c-267d-4ee3-94b6-73b7624840da | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | SupplyAir |  | CommunicationBus | Flow |  |  | 11002 |  |  |  |  | 59 | 1 | 1 | 0 |  | 3 | Actualsupply air flow
427822f1-415b-407a-9063-7b1ebf668fea | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | SupplyAir |  | CommunicationBus | State |  |  | 11002 |  |  |  |  | 60 | 1 | 1 | 0 |  | 3 | Actual supply air state
af845a31-fea3-4318-aeb8-a42525c8605b | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | Indoor |  | CommunicationBus | Temperature |  |  | 11002 |  |  |  |  | 62 | 1 | 10 | 30000 |  | 3 | Actual room temperature
05018ca9-2051-4015-8a89-225e5e3190ad | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | SupplyAir |  | CommunicationBus | Temperature |  |  | 11002 |  |  |  |  | 64 | 1 | 10 | 30000 |  | 3 | Actual supply air temperature
eb943e53-3f78-4733-8855-90309a335c56 | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | Indoor |  | CommunicationBus | Presence |  |  | 11002 |  |  |  |  | 66 | 1 | 1 | 0 |  | 3 | Actual presence (binary)
c20789b3-2a2c-41d9-9025-1a40ece45384 | Sensor | f660f703-6bf4-452f-8b4c-93e71f6ad82a | 63e58b79-eeb2-4717-a66d-2b615e2dea4e |  | SupplyAir |  | CommunicationBus | Pressure |  |  | 11002 |  |  |  |  | 78 | 1 | 10 | 30000 |  | 3 | Actual supply air pressure
8f74f492-c82a-4c22-9c4e-9bd8360b544f | Device |  |  |  |  | AirhandlingUnit | CommunicationBus |  |  | LB01-123-001-001 | 11001 | ModbusTCP | 10.32.6.220 | 502 | 2 |  |  |  |  | Swegon
835f3847-859f-4645-be08-a9670bc4a1e2 | Actuator | 8f74f492-c82a-4c22-9c4e-9bd8360b544f | 1bb52784-c9ed-4d16-b678-63127a02060d |  | SupplyAir |  | CommunicationBus | Temperature | Number |  | 11001 |  |  |  |  | 21 | 1 | 10 | 30000 |  | 3.6 | Setpoint temperature
faecde53-046f-4a39-8256-b24ae1dd04db | Sensor | 8f74f492-c82a-4c22-9c4e-9bd8360b544f | 1bb52784-c9ed-4d16-b678-63127a02060d |  | SupplyAir |  | CommunicationBus | Flow |  |  | 11001 |  |  |  |  | 59 | 1 | 1 | 0 |  | 3 | Actual supply air flow
9c52940c-6dcc-454f-b746-7806b71b9368 | Sensor | 8f74f492-c82a-4c22-9c4e-9bd8360b544f | 1bb52784-c9ed-4d16-b678-63127a02060d |  | SupplyAir |  | CommunicationBus | State |  |  | 11001 |  |  |  |  | 60 | 1 | 1 | 0 |  | 3 | Actual supply air state
8a1bdc87-8e74-4adf-ac78-58768380e1a8 | Sensor | 8f74f492-c82a-4c22-9c4e-9bd8360b544f | 1bb52784-c9ed-4d16-b678-63127a02060d |  | SupplyAir |  | CommunicationBus | Pressure |  |  | 11001 |  |  |  |  | 78 | 1 | 10 | 30000 |  | 3 | Actual supply air pressure
93568657-ab3b-4c80-992c-b61e5dc8a852 | Sensor | 8f74f492-c82a-4c22-9c4e-9bd8360b544f | 1bb52784-c9ed-4d16-b678-63127a02060d |  | SupplyAir |  | CommunicationBus | CO2 |  |  | 11001 |  |  |  |  | 65 | 1 | 1 | 0 |  | 3 | Actual CO2 value
…
UUID that identifies the Device or Sensor or Actuator | Type | A Sensor or Actuator or Device that is a part of another Device | What BuildingStructureComponent (room) the Device or Sensor or Actautaor is located in | A Device serving another Device. E.g. an HVAC-unit serving an air diffuser. | In what context or media that the Sensor or Actuator is operating in | Description of what the main function or purpose is of a Device | The power source for the device | Describes the value observed by a Sensor or the value set by an Actuator | A description of what kind of input the Actuator accepts | Littra on blueprint | The local endpoint ID in a building automation system. "source:" indicates that the data is not needed to be 100% REC compliant | Type of communiaction bus for the Device | Ip address | IP port | Modbus node ID | Modbus register | Modbus register lenght | Sclae factor | Offset | Product type | Modbus function code | Some comments from the blueprint or building automation sytem